# TRITON CLOUD CEILING PANEL

## 1.	GENERAL

### RELATED WORK

1.1	RELATED SECTIONS

Refer to ~ for ~

Documents

### 1.2	DOCUMENTS

Documents referred to in this section are:

NZS 1170	Structural design actions, Earthquake actions – New Zealand

ISO 5660.1 	Cone calorimeter test reaction to fire tests for heat release, smoke production and mass loss rate.

NZBC C/AS1	Fire Safety

AS/NZS 2785	Suspended ceilings - Design and installation

AS 2946	Suspended ceilings, recessed luminaries and air diffusers - Interface requirements for physical compatibility

NZS 4219	Seismic resistance of engineering systems in buildings

ISO 354	Test method for sound absorption by reverberant room method

ISO 11654	Weighted sound absorption ratings

ASTM C423	Test method for sound absorption and sound absorption coefficients by the reverberation room method

ASTM E1414	Standard test method for airborne sound attenuation between rooms sharing a common ceiling plenum (two room method)

ASTM C 635	Standard specification for the manufacture, performance and testing of metal suspension systems for acoustical tile and lay-in panel ceilings

ASTM C636	Standard practice for installation of metal ceiling suspension systems for acoustical tile and lay-in panels

ASTM E413-87	Test method for airborne sound transmission STC

Documents listed above and cited in the clauses that follow are part of this specification.

However, this specification takes precedence in the event of it being at variance with the

cited document.

1.3	MANUFACTURER'S DOCUMENTS

Manufacturer's and supplier's documents relating to work in this section are:

Asona Triton Cloud Panel data sheet

Asona suspension components data sheet

Copies of the above literature are available online at www.asona.co.nz

For lead times and pricing contact Asona Ltd, Unit 14, 7 Cain Road, Penrose, Auckland.

info@asona.co.nz

Telephone:	09 525 6575

Website:	www.asona.co.nz

### Requirements

### 1.4	SAMPLE SECTION

Allow to erect a sample section of the suspended ceiling system offered. Subject to confirmation in writing, the sample section may form part of the completed installation.

Refer to 4. SELECTIONS for location.

### 1.5	INSTALLATION

Minimum installation standard to AS/NZS 2785 and ASTM C636.  Installation to be only by the manufacturer's accredited installer, using the manufacturer's technical services.  Accredited installers to be members of the Association of wall and ceiling industries of New Zealand (AWCI) Provide evidence of experience, listing completed projects of similar size and complexity.

Installation to comply with the requirments of NZS 4219; with related building services installations complying specifically with clauses 2.22, 2.25 and 2.29.

### 1.6	CLEANING INSTRUCTIONS

Clean using soft bristled brush, vacuum or a damp cloth or as noted in product data sheet.

### 1.7	SPARES

Provide spare matching ceiling elements in the quantities specified below.  Deliver into a dry store at the site or elsewhere as directed and at agreed times.  Refer to 4. SELECTIONS for quantity.

### 1.8	SUPPLY WARRANTY

Supply manufacturers 5 year warranty against manufacturing defects and durability compliance per NZBC B2 of 5 years for accessible tiles and 15 years for suspension components.

1.9	NO SUBSTITUTIONS

Substitutions are not permitted to any specified Asona system, or associated components and products.

Performance

### 1.10	LOADING CODE REQUIREMENT

NZS 1170, section 8.

### 1.11	CERTIFICATION

Provide:

- NZS 1170, section 8 for evaluation

-	certificates and other evidence that the system offered complies with the standards of performance specified

-	a Producer Statement on completion.

### 1.12	ACOUSTIC REQUIREMENTS

Verify material sound absorption performance.  Submit a copy of a full scale sound absorption test report to ISO 354 E200 as tested by Auckland Uni Services or other independent testing authority.  Refer to 4. SELECTIONS for acoustic performance requirements.

1.13	REACTION TO FIRE PROPERTIES

Reaction to fire properties of the ceiling system must meet the acceptable solutions to all risk groups C/AS1 to C/AS7. Risk groups:SH, SM, SI, CA, WB, WS, VP

ASONA PRODUCT FIRE GROUP NUMNER RATINGS

ISO 5660-1 Cone Calorimeter test

| ASONA PRODUCTS | TYPE OF MATERIAL | GROUP NUMBER |
| --- | --- | --- |
| Triton Cloud Panel (Sonatex & 1963 Woven Glass Fabric) | Glass fibre ceiling panels | 1S |
| Triton Cloud Panel (Standard Fabrics ) | Glass fibre ceiling panels | 2 |
| Triton Cloud Pool Panel | Glass fibre ceiling panels | 1S |

### 1.14	ENVIRONMENTAL REQUIREMENTS

Design the ceiling system for use over its expected life without deterioration within the required temperature and humidity range.  Refer to 4. SELECTIONS for details.

### 1.15	LIGHT REFLECTANCE

To ASTM C1477.  Refer to SELECTIONS for reflectance and colour.

## 2.	PRODUCTS

Materials – Acoustic ceiling panels

### 2.1	Triton Cloud Panel - HIGH SOUND ABSORBING CEILING PANELS

Manufactured and supplied by Asona Ltd tel: 09 52 56575

Type: Triton Cloud Pool Panel from resin bonded bio soluble glass fibre core and

wrapped in SonatexTM dual layer composite acoustical facer or in 1963 Glass woven

fabric. The panel can be aluminium framed or frameless, panels to be made in NZ from

80% recycled glass waste. Panels fixed to framing via brackets or spiral anchor kits.

## 3.	EXECUTION

Conditions

### 3.1	CO-ORDINATE SERVICES

Co-ordinate and co-operate with electrical and mechanical work to avoid conflict between timber framing, suspension members, luminaires, pipework and ducting. Confirm the provision of extra hangers and fixings.

3.2	SITE CONDITIONS

Do not begin installation until the building is closed in, fully glazed, the roof watertight, and mechanical and electrical duct work above the ceiling completed.

### 3.3	COMPLY

Comply with AS 2946 for interface requirements for physical compatibility.

### 3.4	RESPONSIBILITY

Ensure that conditions are suitable for the ceiling installation. Arrange for the programming of the work to suit required practice.

Application

### 3.5	INSTALL

Install the system to AS/NZS 2785 minimum standards and the ceiling manufacturer's requirements. Panels must have fixings every 1200mm centres. Sub-trades must at no time lean on or use panels for support.

### 3.6	PENETRATIONS

Accommodate recessed light fittings, air conditioning outlets and other electrical and/or mechanical services that are fixed to or pass through the ceiling system.  Provide independent support for these as necessary.  Such fittings are not to be supported by the acoustical ceiling panels.

### 3.7	PROTECT EXISTING WORK

Protect adjacent existing work from damage during the installation.

Completion

### 3.8	REPLACE

Replace or repair damaged or marked elements.  Recycle material, consult manufacturer for replacement facers or painting procedures.

### 3.9	LEAVE

Leave work to the standard required by following procedures.

### 3.10	REMOVE

Remove debris, unused elements and elements from the site.

### 3.11	CLEAN

Clean soiled or marked units.

## 4.	SELECTIONS

Requirements

### 4.1	SAMPLE SECTION

Location:	~

Size:	~ m x ~ m

Facing:             	~

Performance

### 4.2	ACOUSTIC REQUIREMENTS

Practical sound absorption properties to ISO 354 E200, ratings to ISO 11654

| Frequency | 125 Hz | 250 Hz | 500 Hz | 1000 Hz | 2000 Hz | 4000 Hz |
| --- | --- | --- | --- | --- | --- | --- |
| αP | 0.70 | 1.00 | 1.00 | 1.00 | 1.00 | 0.95 |

Sound absorption class:		A

Weighted sound absorption coefficient W:	1.00 minimum

NRC to ASTM C423-99:		1.05 minimum

### 4.3	ENVIRONMENTAL REQUIREMENTS

Range:	10 - 45°C

Relative humidity:	95 % maximum

### 4.4	REFLECTANCE

Reflectance:	LR1 per ASTM 1477, 75 % minimum

For (colour):	White

For other colours & fabrics:  less than 75%

### 4.5	FIRE

Group Number: 1S (ISO 5660.1 Cone calorimeter test)

(using Sonatex or 1963 woven glass fabric only) (Fire rating for fabric wrapped panels is dependent upon fabric used)

Materials

4.6	SCHEDULE

| Area | Product reference | Finish |
| --- | --- | --- |
| ~ | Triton Cloud Panel | Sonatex / 1963 Woven glass fabric / Standard fabric |

Accessible panel with suspended grid systems

### 4.7	CEILING PANEL

Brand/product:	Triton Cloud Panel

Manufacturer:	Asona Ltd, Unit 14, 7 Cain Road, Penrose, Auckland

Tel: 09 525 6575, Fax: 09 525 6579, Email: info@asona.co.nz

Material Type:	Bio soluble resin bonded glass fiber laminated wrapped toughened Sonatex 250 kg/m3 dual layer glass mat composite facer or wrapped in 1963 woven glass fabric or wrapped in standard fabric, with optional foil backing, made in NZ from 80% recycled glass waste.

.

Thickness:	25mm, 40mm, 50mm, 75mm, 100mm

Sizes:

| Size | Thickness |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
|  | 25mm | 40mm | 50mm | 75mm | 100mm |
| 300x1200 | ( ~ ) | ( ~ ) | ( ~ ) | ( ~ ) | ( ~ ) |
| 600x600 | ( ~ ) | ( ~ ) | ( ~ ) | ( ~ ) | ( ~ ) |
| 600x1200 | ( ~ ) | ( ~ ) | ( ~ ) | ( ~ ) | ( ~ ) |
| 600x1800 | ( ~ ) | ( ~ ) | ( ~ ) | ( ~ ) | ( ~ ) |
| 600x2400 | ( ~ ) | ( ~ ) | ( ~ ) | ( ~ ) | ( ~ ) |
| 1000x1200 | ( ~ ) | ( ~ ) | ( ~ ) | ( ~ ) | ( ~ ) |
| 1000x1800 |  | ( ~ ) | ( ~ ) | ( ~ ) | ( ~ ) |
| 1000x2400 |  | ( ~ ) | ( ~ ) | ( ~ ) | ( ~ ) |
| 1000x3000 |  |  | ( ~ ) | ( ~ ) |  |
| 1200x1200 |  | ( ~ ) | ( ~ ) | ( ~ ) | ( ~ ) |
| 1200x1800 |  | ( ~ ) | ( ~ ) | ( ~ ) | ( ~ ) |
| 1200x2400 |  | ( ~ ) | ( ~ ) | ( ~ ) | ( ~ ) |
| 1200x3000 |  |  | ( ~ ) | ( ~ ) |  |
| Custom(m x m) |  | ( ~ ) | ( ~ ) | ( ~ ) | ( ~ ) |

Finish:	(Sonatex plain laminate) (Sonaris perforated laminate)(1963 Woven Glass Fabric)(Standard Fabric)

Edge:	Square

Sonatex Colours: 	Sonatex:(White AS180) (Mid Grey RAL7040) (Light Grey RAL7030) (Grey White RAL9002) (Wood Wool Print) (Plaster Print) (Wood Print over RAL1014 Oak) (Wood Print over RAL1013 Blond) (Wood Print over RAL8019 Walnut) (Zinc Yellow RAL1018) (Ivory RAL1014) (Graphite Black RAL9011)(Traffic Red RAL3020) (Orient Red RAL3031) (Traffic Orange RAL2009) (Traffic Green RAL6032) (Aqua RAL6027) or (1963 White Glass Woven Fibre Fabric ) or standard fabric ranges. Other colours and fabrics to order.

Service panels:	Supply M/E service panels with factory applied proactive film.

Remove on completion of ceiling installation

### 4.8	SUSPENSION

Type:	(Direct fix brackets)

(40mm steel spiral anchors)

(2m galvanized hanger wire),

with adjustable connectors and end-loops).

Spares

### 4.9	SPARES

Panels:	Supply ~ panels on completion